## TOC & Legend
IEC 62381 / ISA-62381 PLC/DCS Functional Test Suite
Generated 2026-08-15 ¦ Version 1.0 (Technical Audit Template)
TABLE OF CONTENTS
Sheet Name | Description | Hyperlink | IEC 62381 Clause Ref
TOC & Legend | Table of contents, model versioning, and cell formatting guidelines. | Go → | N/A
Functional Test Checklist | Complete execution checklists of PLC/DCS software, logic, redundancy, and HMI functions. | Go → | Clause 5.2 / Annex A.3
Punch List Ledger | Audit-ready tracking register for non-conformities, severity categories, and closure gates. | Go → | Clause 5.4 / 3.1.16
PLC Automated Tests | Automated assertion-based functional test execution log, synchronized with PLC Tester. | Go → | Clause 5.2 / Annex A.3
SPREADSHEET COLOR-CODE CONVENTIONS
Visual Representation | Cell Convention | Role in Testing Workflow | Expected User Action
Input Cells | Editable Field | Signals editable cells where testers enter actual values, test dates, and comments. | User-entered
Calculated Cells | Formula-Driven | Computed fields (e.g. sums, counts, percent completion, or lookup results). | Do not modify
Zebra Striping | Alternate Rows | Improves readability for tracking dense rows of test protocols. | Visual guide only
Placeholder Cells | Sample Data | Contains initial placeholder values to demonstrate the sheet logic. Clear to overwrite. | Replace with actual

## Functional Test Checklist
IEC 62381 / ISA-62381 PLC/DCS Functional Test Checklist
Scope: Clause 5.2 / Annex A.3 - Software, Logic, Redundancy, Security, and HMI Functional Tests (Excluding E&I Loop Checks)
TOTAL TEST CASES |  |  | PASSED |  |  | FAILED |  |  | BLOCKED/IP | % COMPLETE
Test Case ID | Annex Ref | Functional Category | Test Activity / Description | Acceptance Criteria / Expected Result | Actual Observed Result | Status | Tester Name | Execution Date | Reference Documents / Notes
TC-FUN-001 | A.3.6 | Start-up & Power | Verify sequence-controlled power-up of PLC cabinet, network switches, and controllers. | System boots to standby mode without CPU faults or illegal logic states. | System booted cleanly with no controller faults. | Passed | S. Iyalunaidu | 2026-08-10 | PDS-SEC-4.1
TC-FUN-002 | A.3.6 | Start-up & Power | Simulate clean shutdown sequence of PLC servers and database historians. | No database corruption; all open communication sessions terminate gracefully. | Verified clean shutdown. Historian files intact. | Passed | S. Iyalunaidu | 2026-08-10 | PDS-SEC-4.2
TC-FUN-003 | A.3.6 | Start-up & Power | Simulate sudden 24VDC power failure and immediate UPS transition. | UPS takes over instantly; system log records power alarm; no CPU restart. | Power supply tripped; UPS took load instantly. CPU runtime un-interrupted. | Passed | S. Iyalunaidu | 2026-08-10 | PDS-PWR-1.2
TC-FUN-004 | A.3.7 | System Alarms | Verify priority alarm generation for critical analog PV out-of-bounds. | HMI displays flash red, high priority horn triggers, alarm is logged in Sequence of Events. | HMI flashed, but audible horn delayed by 4 seconds. | Failed | S. Iyalunaidu | 2026-08-11 | PL-001 (See Punch List)
TC-FUN-005 | A.3.7 | System Alarms | Verify operator 'Shelve/Suppress' function on active low-priority alarms. | Alarm visual changes to shelved state; suppressed alarm does not trigger horn. | Verified. Active alarms successfully shelved and removed from main banner. | Passed | S. Iyalunaidu | 2026-08-11 | HMI-STD-Ch3
TC-FUN-006 | A.3.7 | System Alarms | Verify Sequence of Events (SOE) timestamp accuracy under rapid multi-alarm bursts. | Timestamp resolution is within 1ms millisecond range for precise event ordering. | Verified SOE timestamp resolution is at 1ms level. | Passed | S. Iyalunaidu | 2026-08-11 | PDS-SOE-2.0
TC-FUN-007 | A.3.8 | Redundancy & Failover | Simulate primary CPU controller hardware failure (unplug power / extract module). | Secondary hot-standby CPU takes mastership within 500ms; zero process disruption. | Switchover completed but took 1.2s, which exceeded 500ms target. | Failed | S. Iyalunaidu | 2026-08-12 | PL-002 (See Punch List)
TC-FUN-008 | A.3.8 | Redundancy & Failover | Disconnect primary ring fiber link on redundant control network. | Redundant ring path heals automatically; HMI logs network diagnostic warning. | Ring path healed immediately. Zero lost packets. | Passed | S. Iyalunaidu | 2026-08-12 | PDS-NET-3.5
TC-FUN-009 | A.3.8 | Redundancy & Failover | Verify redundant power supply load sharing (disconnect Power Supply A module). | Power Supply B continues to power complete cabinet load without voltage dip. | Verified. Load seamlessly carried by Power Supply B. | Passed | S. Iyalunaidu | 2026-08-12 | PDS-PWR-2.1
TC-FUN-010 | A.3.9 | HMI / Graphics | Test navigation link transition times and screen load times under peak load. | All control displays and faceplates open in less than 1.0 second. | Verified screen load times under 1 second. | Passed | S. Iyalunaidu | 2026-08-13 | HMI-STD-Ch1
TC-FUN-011 | A.3.9 | HMI / Graphics | Validate entry limit validation popup (input value beyond high/low clamp limits). | HMI rejects input, displays 'Out-of-Range' tooltip; prevents invalid PLC download. | Verified limits. Text field rejects out of range inputs. | Passed | S. Iyalunaidu | 2026-08-13 | HMI-STD-Ch2
TC-FUN-012 | A.3.9 | HMI / Graphics | Verify HMI dynamic object behavior and alarm color rendering consistency. | Failed states render as red flashing; normal states green; disabled as gray. | Verified static and dynamic states. | Passed | S. Iyalunaidu | 2026-08-13 | HMI-STD-Ch5
TC-FUN-013 | A.3.11 | User Management | Verify User Profile permissions (Operator vs. Engineer vs. Admin roles). | Operators cannot edit interlocks; Engineers cannot edit system config; Admins have full access. | Verified Role-Based Access Control (RBAC) restrictions. | Passed | S. Iyalunaidu | 2026-08-14 | PDS-SEC-1.1
TC-FUN-014 | A.3.11 | User Management | Verify inactive console automatic workstation session timeout and logout. | Console locks automatically after 15 minutes of user inactivity. | Verified. Auto-logout triggered at exactly 15 minutes. | Passed | S. Iyalunaidu | 2026-08-14 | PDS-SEC-1.2
TC-FUN-015 | A.3.12 | System Security | Perform audit of active software ports and disable unused physical Ethernet/USB ports. | All unused ports are logically disabled; BIOS is password protected. | Verified ports are locked down in firmware. | Passed | S. Iyalunaidu | 2026-08-14 | IEC 62443-3-3 SR4
TC-FUN-016 | A.3.18 | Subsystem Links (FIT) | Verify Modbus TCP communication registers mapping from OEM compressor PLC. | Address offsets match mapping database; Float values scale and display correctly on DCS HMI. | Communication link established; data registers mapped successfully. | Passed | S. Iyalunaidu | 2026-08-14 | PDS-FIT-6.1
TC-FUN-017 | A.3.18 | Subsystem Links (FIT) | Simulate OEM compressor PLC watchdog loss and heartbeat timeout diagnostics. | Main DCS HMI generates 'OEM COMMS LOST' priority alarm within 3 seconds of watchdog loss. | Heartbeat timeout triggered DCS alarm after exactly 2.5 seconds. | Passed | S. Iyalunaidu | 2026-08-14 | PDS-FIT-6.2
TC-FUN-018 | A.3.19 | Application Logic | Verify Emergency ESD cause-and-effect matrix interlock logic. | Activating manual ESD mushroom button overrides HMI commands, closes all target valves under 1s. | Verification pending - scheduled for final day of FAT. | In Progress | S. Iyalunaidu | 2026-08-14 | PDS-ESD-2.0
TC-FUN-009
TC-FUN-010
TC-FUN-011
TC-FUN-012
TC-FUN-013
TC-FUN-014
TC-FUN-015
TC-FUN-016
TC-FUN-017
TC-FUN-018
TC-FUN-019
TC-FUN-020

## PLC Automated Tests
IEC 62381 / ISA-62381 PLC Automated Test Ledger
Scope: Clause 5.2 / Annex A.3 - PLC Tester Automated Assertion-Based Functional Tests (Standard Compliance: IEC 62381:2024 / ISA-62381-2026)
SYSTEM CONFIGURATION BASELINE (CONFIGURATION CONTROL) |  |  |  |  | TEST EXECUTION STATS (DYNAMIC KPIs)
PLC CPU Node ID: | PLC-01-CV_CTRL | Application Checksum (SHA-256): | 0x8F3D11A7B2C9 | Network Load Status: | TOTAL PLC TESTS | PASSED | FAILED | PASS RATE
Firmware Revision: | v21.05.12 | Tag Database Version: | DB-Build-2026-v1.4 | Stress Test (FIT Mode)
Test ID | Design Ref | Test Scenario & Behavioral Description | Pre-Condition Tag | Pre-Condition Val | Trigger Tag | Trigger Val | Wait Time (ms) | Expected Tag | Expected Val | Analog Tolerance | Fail-Safe State | Actual Observed Response | Status | Auditor | Execution Date | Punch List Ref
TC-001 | URS Clause 4.2.1 | Test Blocked Chute 2s Delay (Conveyor running, chute switches to blocked. Alarm must trip after 2s delay to prevent false trips) | CV001_Run_Cmd | 1 | CS001_Input | 1 | 2500 | CV001_Trip_Alm | 1 | N/A (Digital) | Conveyor Motor De-energized | Alarm tripped after 2040ms. Conveyor stopped safely. | Pass | S. Iyalunaidu | 2026-08-15 | N/A
TC-002 | URS Clause 4.2.1 | Test Blocked Chute False Trip (Conveyor running, transient blocked signal injected for 1s. Alarm must NOT trip) | CV001_Run_Cmd | 1 | CS001_Input | 1 | 1000 | CV001_Trip_Alm | 0 | N/A (Digital) | Conveyor Continues Running | Transient signal ignored, motor remained active. Correct delay validation. | Pass | S. Iyalunaidu | 2026-08-15 | N/A
TC-003 | URS Clause 4.2.3 | Test Run Off 10s Delay (Conveyor run-off switch activated. Minor interlock alarm must trip after 10s delay) | CV001_Run_Cmd | 1 | RO001_Input | 1 | 10500 | CV001_Minor_Ilk | 0 | N/A (Digital) | Minor interlock safety alarm active | Interlock failed to activate within 10s delay. Signal read as 0. PLC logic block CV001_CTRL fails to process. | Fail | S. Iyalunaidu | 2026-08-15 | PL-003
TC-04
TC-05
TC-06
TC-07
TC-08
TC-09
TC-010
TC-011
TC-012
TC-013
TC-014
TC-015

## Punch List Ledger
IEC 62381 / ISA-62381 Punch List Ledger
Classification: Category A - Hold-point (Must resolve before shipment); Category B - Minor (Can carry over to SAT/SIT)
TOTAL OPEN ITEMS |  |  | CATEGORY A (HOLD) |  |  | CATEGORY B (MINOR) |  | TOTAL ITEMS | VERIFICATION RATE
Punch ID | Checklist Ref | Non-Conformance Description | Severity Class | Assigned Owner | Target Close Date | Status | Resolution & Verification Details
PL-001 | TC-FUN-004 | High-priority critical analog alarm triggered on HMI, but the physical control room audible horn was delayed by 4 seconds (Standard target: instant horn trigger). | A - Hold-point | Automation Vendor | 2026-08-13 | In Progress | Vendor team analyzing Horn relay and block logic timing. Fixed delay settings; pending final re-test.
PL-002 | TC-FUN-007 | Hot-standby CPU controller switchover completed but took 1.2 seconds, exceeding the 500ms target during primary power interruption simulation. | A - Hold-point | CPU OEM Specialist | 2026-08-14 | Open | Analyzing redundant network packet polling interval settings to speed up synchronization.
PL-003 | TC-003 | Minor conveyor run-off interlock (CV001_Minor_Ilk) failed to activate after the 10-second timer delay had elapsed during dynamic conveyor logic testing. Value remained at 0. | B - Minor | PLC Application Programmer | 2026-08-18 | Open | Assigned to application programming team to audit the timer accumulators and internal interlock permissive logic in block CV001_CTRL.
PL-004
PL-005
PL-006
PL-007
PL-008
PL-009
PL-010
PL-011
PL-012
PL-013
PL-014